## Slide 1
Impact of Imperfect Proof Testing on the Performance of Safety Instrumented Functions
EUR ING Ben Easton CEng MIET
ProSalus Limited
(Industrial Partners with Normetic)
12-13 September 2023

## Slide 2
About me
EUR ING Ben Easton CEng MIET, FS Expert (TÜV Rheinland, #299/19, SIS, PH & RA).
Managing Director & Principal Safety Consultant of ProSalus Limited, United Kingdom
I am a TÜV Certified Functional Safety Expert with over 15 years’ experience on projects in Pharmaceutical, Oil and Gas, Agri-chemical, Renewable Energies and Defence industrial sectors within the UK and internationally (including Australia, Canada, Dubai and Europe). I am a Visiting Lecturer at the University of Sheffield on the MSc in Process Safety and Loss Prevention.
I am an active member of:
IET System Safety TPN Committee Executive Member
ISO/TC67/WG4/PG3: ISO TR 12489 “Reliability Modelling and Calculation of Safety Systems”
The 61508 Association Executive Member
BSI GEL/065/05: Devices and integration in enterprise systems
IET Professional Registration Mentor

## Slide 3
Agenda
Section | Description
I. | What is Proof Test Coverage?
II. | Why is Proof Test Coverage Important?
III. | How is Proof Test Coverage calculated?
IV. | How do we incorporate Proof Test Coverage into our calculations?
V. | Conclusion
VI. | References

## Slide 4
What is Proof Test Coverage?
To understand Proof Test Coverage, it must be first understood what is a proof test.
A Proof Test is defined by IEC 61511 as ‘a periodic test performed to detect dangerous hidden faults in a SIS so that, if necessary, a repair can restore the system to an ‘as new’ condition or as close as practical to this condition’

## Slide 5
What is Proof Test Coverage?
Proof Test Coverage
The percentage of that can be identified through proof testing is the proof test coverage.
With all remaining remaining undetected until there is a demand on the system, or the system undergoes ‘workbench’ maintenance and is restored to ‘as new’ condition.
Chart: 
| λ_s | λ_dd | λ_du (Cpt) | λ_du (1-Cpt)
Failure Rate Ratio | 0.70304 | 0.04373 | 0.029013 | 0.029013

## Slide 6
What Impacts Proof Test Coverage?
Systematic failures impacting on the hardware capability:
  SIF designed to permit required testing
    Pre-IEC 61508:2010 equipment; knowing undiagnosed failure mode to test for
  Introduction failure modes due to operations and maintenance
  Extension of major maintenance interval; potentially into the wear failures in the bath tub curve
  Use of generic proof tests not covering equipment specific failure modes
  Modification to diagnostic capability (know / unknown)
Accumulation of failure modes impacting on the safety path, due to poor inspection, or poor maintenance.

## Slide 7
How is Proof Test Coverage determined
SAFETY MANUAL – PROOF TEST
Endress Hauser – Functional Safety Manual [Ref 3]

## Slide 8
How is Proof Test Coverage calculated?
Failure Mode Effect Diagnostic Analysis (FMEDA) – FMEDA EXTRACT for PTC determination
FMEDA For Actuators-Various Based on Norbro Single Acting Spring return |  |  |  |  |  |  |  |  |  |  |  |  | 
ID. | Identification | Function | Failure | Operational |  |  | Failure Effect | Detected by Diagnostic | Detection Method |  |  |  | Compensating
 |  |  | Modes | Mode | Local | End | Safe / Dangerous |  | Auto Diagnostic | Detected by Proof Test | Function Test | Other | Provisions
1 | Body | Provides mechanical protection to internal parts and forms part of the overall structure of the actuator. | Defect in body at time of manufacture. | Deployment, commissioning | Loss of sealing resulting in air leak, reduced operation/effectiveness of the actuator. | Failure of equipment, reduced stroke. | Dangerous | Undetected | None | YES | Visual inspection of the operation of the actuator during the proof test would reveal leak, non smooth or reduced operation. | Maintenance overhaul once ever 10 years. | Actuator operation will be inspected during installation, commissioning and re-testing. If limit switches were fitted, then this may identify reduced movement.
2 | Pinion | Part of 'rack & pinion' which results in actuator movement as a result of either air pressure or spring return. | Defect in seal at time of manufacture. | Deployment, commissioning | Reduced/incorrect movement of the actuator. | Actuator dose not achieve full stroke. | Dangerous | Undetected | None | YES | Visual inspection of the operation of the actuator during the proof test would reveal incorrect alignment and/or reduced stroke | Maintenance overhaul once ever 10 years. | Actuator operation will be inspected during installation, commissioning and re-testing. If limit switches were fitted, then this may identify reduced movement.
6 | Bearing | Guides the support rod to ensure smooth movement. | Corrosion / erosion from external environmental conditions. | Environmental extremes | Water or liquid ingress leading to long term corrosion. | Failure of equipment. | Dangerous | Undetected | None | NO | This type of degradation maybe over a period and may not be detected during the early years/proof tests, so would eventually be picked up during a later proof test. For this reason, no credit taken for detection during the proof test. | Maintenance overhaul once ever 10 years. | Proof tests later on in the operating life of the component might identify the failure.
Total |  |  |  |  |  |  | Dangerous | Total Dangerous Detected |  | Total Dangerous Detected by Proof Test |  |  | 
 |  |  |  |  |  |  | 29 | 0 |  | 27 |  |  | 
 |  |  |  |  |  |  | Safe | Total Dangerous Undetected |  | Total Dangerous Undetected by Proof Test |  |  | 
 |  |  |  |  |  |  | 3 | 29 |  | 2 |  |  | 

## Slide 9
How is Proof Test Coverage incorporated into PFDAVG?
Calculation composition

## Slide 10
How is Proof Test Coverage incorporated into PFDAVG?
Example Modified ISA TR84.002 (after logic method)
Abbreviations
DC = Diagnostic Coverage Di = Diagnostic Interval. = Dangerous Failure Rate
PCT = Proof Test Coverage Factor. MRT = Mean Repair Time MT = Mission Time
Architecture | “Average before” PFDAVG formulas for voting configuration with consideration of CCF, diagnostics, MTTR, PTC and MTi
1oo1 | 
1oo2 | 
1oo3 | 
2oo2 | 
2oo3 | 
3oo3 | 
Architecture | “Average before” PFDAVG formulas for voting configuration with consideration of CCF, diagnostics, MTTR, PTC and MTi
1oo1 | 
1oo2 | 
1oo3 | 
2oo2 | 
2oo3 | 
3oo3 | 

## Slide 11
Why is Proof Test Coverage Important?
 | Architecture | Failure Rate (λD) | Failure Rate (λDU PTC) | Failure Rate (λDD PTC) | DC | CCF | PTC | Di | MTTR | Misson Time | Ti | PFDavg
 |  | 1/hr | 1/hr | 1/hr | % | β | % | ms | hr | years | yr | Total
Pressure Transmitter E+H PMD70 (FAIL HIGH) | 2oo3 | 1.14E-06 | 3.42E-07 | 7.99E-07 | 70% | 15% | 99% | 100 | 24 | 15 | 1 | 2.67E-04
Logic Solver | 1oo1 | 5.71E-07 | 5.71E-08 | 5.14E-07 | 90% | 0% | 95% | 100 | 24 | 20 | 1 | 5.01E-04
Solenoid | 1oo2 | 3.42E-06 | 3.42E-06 | 0.00E+00 | 0% | 10% | 84% | 0 | 24 | 6 | 1 | 3.30E-03
Final Element (Actuator & Valve Assembly) | 1oo1 | 1.48E-07 | 1.48E-07 | 0.00E+00 | 0% | 0% | 60% | 0 | 72 | 6 | 1 | 1.96E-03
Total PFD |  |  |  |  |  |  |  |  |  |  |  | 6.03E-03
RRF |  |  |  |  |  |  |  |  |  |  |  | 166
Hardware SIL Capability |  |  |  |  |  |  |  |  |  |  |  | SIL 2
 | Architecture | Failure Rate (λD) | Failure Rate (λDU PTC) | Failure Rate (λDD PTC) | DC | CCF | PTC | Di | MTTR | Misson Time | Ti | PFDavg
 |  | 1/hr | 1/hr | 1/hr | % | β | % | ms | hr | years | yr | Total
Pressure Transmitter E+H PMD70 (FAIL HIGH) | 2oo3 | 1.14E-06 | 3.42E-07 | 7.99E-07 | 70% | 15% | 100% | 100 | 24 | 15 | 1 | 2.34E-04
Logic Solver | 1oo1 | 5.71E-07 | 5.71E-08 | 5.14E-07 | 90% | 0% | 100% | 100 | 24 | 20 | 1 | 2.64E-04
Solenoid | 1oo2 | 3.42E-06 | 3.42E-06 | 0.00E+00 | 0% | 10% | 100% | 0 | 24 | 6 | 1 | 1.69E-03
Final Element (Actuator & Valve Assembly) | 1oo1 | 1.48E-07 | 1.48E-07 | 0.00E+00 | 0% | 0% | 100% | 0 | 72 | 6 | 1 | 6.61E-04
Total PFD |  |  |  |  |  |  |  |  |  |  |  | 2.85E-03
RRF |  |  |  |  |  |  |  |  |  |  |  | 351
Hardware SIL Capability |  |  |  |  |  |  |  |  |  |  |  | SIL 2

## Slide 12
Why is Proof Test Coverage Important?
Reduction to achieve PFDAVG and therefore achieved risk reduction.
SIF maintenance overhaul period now set as part of the PFDAVG calculation, therefore now critical part of safety performance standards.
Increased reliance on correct application of proof test procedure so as not to introduce systematic failure.
Increased reliance on the requirement to conduct functional safety audits on proof test procedures and implementation.
Highlighted requirements for the competency of the Design, installation, commissioning, operation and maintenance teams are essential to achieve Proof Test Coverage with respect to systematic failures.

## Slide 13
Competency in relation to PTC
The competency of the persons involved in all lifecycle aspects can have significant impact on the SIF’s ability to provide the required risk reduction. Persons participating in all aspects of the proof testing process should have:
clearly demonstrable competency to carry out their allotted task.
clearly identified and communicated responsibilities and
documented verification that the proof test is suitable and sufficient in terms of content and execution.
If the proof test is developed by a person who lacks the required knowledge and understanding, there is an increased probability that elements essential to the safety path may be excluded from the proof test, therefore, decreasing the PTC. Equally if the person conducting the proof test does not fully understand or appreciate why they are conducting the test, or elements of the test, there is an increased probability that the PT will be inadequately completed and, therefore, decrease the actual risk reduction the SIF is providing.

## Slide 14
Conclusion
Achieving perfect Proof Test Coverage is nearly impossible, therefore base assumption of simplified formulas are inaccurate.
Not Considering Proof Test Coverage early in the lifecycle can lead to not achieving Risk Reduction Requirements.
Where Proof Test Coverage Factor is not freely available (Safety Manual), FMEDA should be adopted, if not possible then a guidance tool such as that identified in T996 should be adopted to provide assurances and assumptions for the design to be based on.
Competency of the Design, installation, commissioning, operation and maintenance teams are essential to achieve Proof Test Coverage with respect to systematic failures.

## Slide 15
References
IEC 61511:2016 – Functional Safety – Safety Instrumented Systems for the process industry sector (Parts 1-3)
American National Standards Institute, FCI 70-2: Control Valve Seat Leakage
Endress + Hauser, Deltabar S, Functional Safety Manual, Differential Pressure, Level and Flow Measurement, PMD70, PMD75, FMD76, FMD77, FMD78
Dr David J. Smith and Kenneth G.L. Simpson, The Safety Critical Systems Handbook, Butterworth-Heinemann, Fifth Edition, 2020, ISBN: 978-0-12-820700-0
Technis / ProSalus, Guidelines on Assessing Proof Test Coverage, Technis Guideline No T996, Issue 1.0, September 2020.
ISA-TR84.00.02-2015, Safety Integrity Level (SIL) Verification of Safety Instrumented Functions, Technical Report, Approved 8th September 2015
Nunns, S. (2002). CRR 428/2002 Principles for proof testing of safety instrumented systems in the chemical industry. HSE. Billingham: HSE.
Interpretative Standard - Proof Testing of Safety Instrumented System in the Onshore Chemical / Specialist Industry (http://hse.gov.uk/foi/internalops/og/og-00054.htm)
Principles of proof testing of safety instrumented systems in the chemical industry (http://www.hse.gov.uk/research/crr_htm/2002/crr02428.htm)

## Slide 16
FUAR İÇİ 41040 IZMIT/KOCAELİ
TEL: +90 262 315 80 00
FAX: +90 262 321 90 70
WEB: www.kosano.org.tr
E-MAIL: kso@kosano.org.tr